## READ ME
Attachment 2-1. READ ME
For use in the WQIP Annual Report's MS4 Outfall Discharge Assessments (WQIP Section 4.2.3), please fill in Jurisdictional Knowedge tabs with your jurisdictional follow up and knowledge regarding these outfalls.
Instructions for each tab
Identify Controllable Sources:
WHY: Per WQIP Section 4.2.3.1.1
WHAT: Requesting general knowledge of persistent and transient flow in your jurisdiction
HOW: In the yellow columns, describe what you learned from field screening, JRMP Annual Reporting, unnatural water balance HPWQC strategies, and/or any other strategies
Identify Sources of NALs Exceedances:
WHY: Per WQIP Section 4.2.3.1.3
WHAT: Requesting knowledge regarding the highest priority major MS4 outfalls that are in exceedance of NALs
HOW: In the yellow columns, describe sources contributing to NALs exceedances at the highest priority outfalls (WQIP Section 4.2.3.1.3). Sampled outfalls are provided in Appendix M. Potential sources are identified as check boxes in Column F. If possible, include the percent contribution of each source.
Persistent Flow % Contribution
WHY: Per WQIP Section 4.2.3.1.4
WHAT: Requesting % contribution from each known source at the major MS4 outfalls found to have persistent dry weather flows this monitoring year
HOW: In the yellow columns, if possible include the percent contribution of each source, if possible. Outfalls with persistent flow conditions are highlighted yellow.
Additional Resources:
To view field screening photos and field screenings from past monitoring years, filter for your jurisdiction at the below dashboard: Field Screening Dashboard

## Identify Controllable Sources
Attachment 2-1. Identify Controllable Sources
Identify Controllable Sources of Transient and Persistent Flows (WQIP Section 4.2.3.1.1.)
Information sources to describe controllable sources of transient and persistent Flows |  | Describe what you learned about known and suspected controllable sources (i.e., facilities, areas, land uses, and pollutant-generating activities) of transient and persistent flows | Describe sources of transient and persistent flows that have been reduced or eliminated | Identify any modifications of the field screening monitoring locations and frequencies to identify and eliminate sources of persistent flow non-stormwater discharges
Dry Weather MS4 Outfall Discharge Field Screening Data | ------------->
JRMP Annual Reports (facility inspections, responses to stormwater hotline calls and public complaints) | -------------> |  | For example: non-permitted discharges/connections removed
Data Obtained via Strategies (Outfall Capture Feasibility Studies, Flow Ecology Study, Inventory of Permitted Discharges and Water Impoundments)1 | ------------->
Other (e.g. water district's rebate programs)2, 3 | -------------> |  | For example: rebate programs, other non-permitted discharges/connections removed
1Inventory of Permitted Discharges and Water Impoundments
2SoCal Water Smart
3SoCal Water Smart Commercial
4 h2oc (Show Me My Watershed)

## Identify Sources of NALs Exceed
Attachment 2-1. Identify Sources of NALs Exceed
Identify Sources Contributing to NAL Exceedances at the Highest Priority Outfalls (WQIP Section 4.2.3.1.3)
Outfall Monitoring Data |  |  |  |  | Outfall catchment percentages |  |  | Identify Sources Contributing to NAL Exceedances at the Highest Priority Major Outfalls |  | Identify Per Cent Contribution of Sources Contributing to NAL Exceedances at the Highest Priority Outfalls
Facility Identifier | Sampling Date | NAL Exceedance (sampled outfall) | Flow Condition | Sp. Conductivity (uS/cm) | Percent catchment in your jurisdiction | Jurisdiction of Discharge Point | Other jurisdictions within catchment | Identify Sources Contributing to NAL Exceedances at the Highest Priority Major Outfalls | Comments | Groundwater or tidal influence | Permitted Discharge: Reclaimed Water | Permitted Discharge: Potable Water | Irrigation Runoff: Reclaimed Water | Irrigation Runoff: Potable Water | Facility Discharge: Reclaimed Water | Facility Discharge: Potable Water | Illicit Connections | Unknown | Other
Fecal Coliform, Enterococci, Total Nitrogen, Total Phosphorous
Fecal Coliform, Enterococci, Total Nitrogen, Total Phosphorous
Fecal Coliform, Enterococci, Total Nitrogen, Total Phosphorous, Iron, Manganese
OCFS and or Flow Ecology Study found groundwater contributes to flow
CHWSRS sampling found HF183 presence
Comments in field screening noted curb run-off
Other (see comments)
Reclaimed water widely used in catchment
Illicit Connections
Permitted Discharge: Reclaimed
Permitted Discharge: Potable
Facility Discharge: Reclaimed
Irrigation Runoff: Reclaimed
Irrigation Runoff: Potable
Facility Discharge: Potable
Unknown
OCFS and or Flow Ecology Study found groundwater contributes to flow
CHWSRS sampling found HF183 presence
Comments in field screening noted curb run-off
Other (see comments)
Reclaimed water widely used in catchment
Illicit Connections
Permitted Discharge: Reclaimed
Permitted Discharge: Potable
Facility Discharge: Reclaimed
Irrigation Runoff: Reclaimed
Irrigation Runoff: Potable
Facility Discharge: Potable
Unknown
OCFS and or Flow Ecology Study found groundwater contributes to flow
CHWSRS Sampling found HF183 presence
Comments in field screening noted curb run-off
Other (see comments)
Reclaimed water widely used in catchment
Illicit Connections
Permitted Discharge: Reclaimed
Permitted Discharge: Potable
Facility Discharge: Reclaimed
Irrigation Runoff: Reclaimed
Irrigation Runoff: Potable
Facility Discharge: Potable
Unknown

## PotentialSources (hidden)
Potential Sources
Reclaimed water widely used in catchment
Comments in field screening noted runoff
OCFS and or Flow Ecology Study found groundwater contributes to flow
CHWSRS sampling found HF183 presence
Permitted Discharge: Reclaimed Water
Permitted Discharge: Potable Water
Irrigation Runoff: Reclaimed Water
Irrigation Runoff: Potable Water
Facility Discharge: Reclaimed Water
Facility Discharge: Potable Water
Illicit Connections
Unknown
Other

## Persistent Flow % Contribution
Attachment 2-1. Persistent Flow % Contribution
Estimate the percent contritution from each known source for each MS4 outfall with persistent flow (WQIP Section 4.2.3.1.4). --------------->
Field Screening Observations | [24 empty] | Jurisdictional Knowledge
Facility Identifier | AvgDischarge (cfs, floating leaf) | Inspection Date | Flow Condition | Persistent Flow | Connectivity to Receiving Water | Priority (Appendix J) | PrioritizationScore | Sp. Conductivity (uS/cm) | Discharge (cfs, floating leaf) | Discharge (cfs, volumetric) | Discharge Trend | Scour Pond Water Condition | Dissipator Water Condition | Comments | Trash Condition | Trash Location | Dry MS4 Discharge Sampling (highest priority major outfall) | Wet MS4 Discharge Sampling (highest priority major outfall) | Outfall Capture Feasibility Study | Maintenance Issues | POINT_Y | POINT_X | SWN sensor location | Date Jurisdictional Manager contacted | Comments Describe what you found | Per cent Groundwater or tidal influence | Per cent Permitted Discharge: Reclaimed Water | Per cent Permitted Discharge: Potable Water | Per cent Irrigation Runoff: Reclaimed Water | Per cent Irrigation Runoff: Potable Water | Per cent Facility Discharge: Reclaimed Water | Per cent Facility Discharge: Potable Water | Percent Illicit Connections | Per cent Unknown | Per cent Other
*Schedule shared at WQIP meetings (), in an email to all on , and also in an email to each jurisdictional managers (emails sent to jurisdiction on 0).

## SourceObsCategoriesSum
| Number of outfalls with NAL exceedances | Reclaimed water widely used in catchment | Comments in field screening noted runoff | OCFS and or Flow Ecology Study found groundwater contributes to flow | CHWSRS sampling found HF183 presence | Permitted Discharge: Reclaimed Water | Permitted Discharge: Potable Water | Irrigation Runoff: Reclaimed Water | Irrigation Runoff: Potable Water | Facility Discharge: Reclaimed Water | Facility Discharge: Potable Water | Illicit Connections | Unknown | Other
Dana Point | 2 | [6 empty] | 2 |  |  |  |  | 2
Aliso Viejo | 10 | 10 | [5 empty] | 10 | 10 |  |  |  | 10
Mission Viejo | 8 | 11 |  | 4 | 4 |  |  | 2 | 2 |  |  |  | 12
Laguna Beach | 4 | [11 empty] | 4
Rancho Santa Margarita | 10 | [6 empty] | 10 | 10 |  |  |  | 10
Laguna Woods | [12 empty] | 3
Laguna Niguel |  | 10 | [5 empty] | 10 | 10 |  |  |  | 10
San Clemente | [8 empty] | 4 |  |  |  | 9
Unincorporated | 12 |  |  | 2 |  |  |  | 12 | 12 |  |  |  | 12
Laguna Hills
San Juan Capistrano | 6 |  |  | 1 |  |  |  |  | 6 |  |  | 1 | 11 | 15
Lake Forest | 7
|  | Reclaimed water widely used in catchment | Comments in field screening noted runoff | OCFS and or Flow Ecology Study found groundwater contributes to flow | CHWSRS sampling found HF183 presence | Permitted Discharge: Reclaimed Water | Permitted Discharge: Potable Water | Irrigation Runoff: Reclaimed Water | Irrigation Runoff: Potable Water | Facility Discharge: Reclaimed Water | Facility Discharge: Potable Water | Illicit Connections | Unknown | Other
| Total | 31 | 0 | 7 | 4 | 0 | 0 | 46 | 54 | 0 | 0 | 1 | 83 | 15